SECTION A: RESPONDENT INFORMATION

| 1. Position/Job Role | Maintenance Technician (sample response) |
| --- | --- |
| 2. Years of experience | 7–10 years |
| 3. Department/Unit | Water Treatment |
| 4. Type of industry/company | Food Processing / Carbonated Soft Drink Bottling |
| 5. How often do you interact with the machine? | Daily |

SECTION B: MACHINE IDENTIFICATION AND GENERAL INFORMATION

| 1. Machine name/type | Water Treatment (Reverse Osmosis) Unit |
| --- | --- |
| 2. Machine identification/asset number | SU-WT-RO-01 (sample asset ID – verify from plant asset register) |
| 3. Manufacturer | Imported bottling-equipment OEM (sample) |
| 4. Model number | RO-30 (sample) |
| 5. Serial number | SN-2012-0101 |
| 6. Date/year of manufacture | 2012 |
| 7. Date/year installed/commissioned | 2013 |
| 8. Age | More than 10 years |
| 9. Locally manufactured or imported? | Imported |
| 10. Main function | Purifies incoming water by filtration and reverse osmosis so it meets the quality needed for syrup and drink production. |
| 11. Normal operating capacity | About 30 m³ of treated water per hour (representative; verify plant record) |
| 12. Normal operating hours per day | 14–18 hours (representative production schedule; verify plant record) |
| 13. Operating days per week | 6 days (representative; verify plant schedule) |

SECTION C: MACHINE OPERATING PARAMETERS

| Parameter | Monitored? | How measured / typical observation |
| --- | --- | --- |
| Temperature | Yes | Feed-water temperature sensor on panel/PLC |
| Vibration | No | Not monitored routinely; checked by touch/listening only |
| Pressure | Yes | Feed, membrane and reject pressure transmitters |
| Speed/RPM | No | Not applicable – fixed-speed pump |
| Voltage | Yes | Panel voltmeter / PLC monitoring |
| Current | Yes | High-pressure pump ammeter on panel |
| Power consumption | Yes | Energy meter on panel |
| Oil level | No | Not monitored on this machine |
| Oil pressure | No | Not monitored on this machine |
| Fuel consumption | No | Not applicable – electric machine |
| Hydraulic pressure | No | No hydraulic subsystem fitted |
| Noise/sound | No | Not monitored; operator listening only |
| Load | No | Not monitored on this machine |
| Flow rate | Yes | Permeate and reject flow meters |
| Other | Yes | Conductivity/TDS, membrane differential pressure, recovery rate |

| 2. Normal operating temperature | About 28 °C (feed water) |
| --- | --- |
| 3. Temperature at which abnormal behaviour begins | About 40 °C (membrane risk) |
| 4. Normal operating speed/RPM | Not applicable – fixed-speed pump (motor 2,900 RPM) |
| 5. Normal operating pressure | Membrane feed about 12 bar (representative) |
| 6. Normal vibration level, if known | Not measured routinely; about 3 mm/s RMS expected for a healthy pump – investigate a sustained rise above baseline. |
| 7. Other important machine parameters | Conductivity/TDS, membrane differential pressure, recovery rate, permeate flow. |
| 8. Are parameters recorded electronically? | Yes – PLC/HMI. |
| 9. If yes | Sensors + PLC/HMI; logbook for cleaning and changes. |

SECTION D: MACHINE MAINTENANCE PRACTICES

| 1. Main maintenance type | Combination |
| --- | --- |
| 2. Routine maintenance frequency | Weekly; major service per manufacturer/plant schedule |
| 3. Recommended service interval | 4,000 operating hours |
| 4. Date of last major service | 14 August 2026 (sample) |
| 5. Date of next scheduled service | 14 February 2027 (sample) |
| 6. Maintenance activities | Membrane cleaning (CIP); cartridge filter change; pump and seal checks; dosing-pump calibration; conductivity-probe calibration; electrical inspection. |
| 7. Who performs maintenance? | Company maintenance personnel |
| 8. Is a maintenance logbook kept? | Yes |
| 9. Are previous machine faults recorded? | Often |
| 10. Usefulness of maintenance history for diagnosis | Very useful |

SECTION E: MACHINE FAILURE AND FAULT HISTORY

| 1. Has the machine experienced a major failure? | Yes (sample response) |
| --- | --- |
| 2. Fault frequency | Occasionally (representative response; verify actual maintenance records) |
| 3. Most common faults | Membrane fouling; high-pressure pump seal leaks; cartridge filter clogging; dosing-pump faults. |
| 4. Component that fails most frequently | RO membranes |
| 5. Date of most recent failure | 22 July 2026 (sample) |
| 6. Cause of most recent failure, if known | Membrane fouling from scaling. |
| 7. Downtime after failure | 4–12 hours |
| 8. Action taken to restore the machine | Membranes chemically cleaned, filters replaced. |
| 9. Was the failure predictable? | Yes |
| 10. Warning signs observed | Rising membrane pressure, falling permeate flow, rising conductivity. |

SECTION F: MACHINE BEHAVIOUR BEFORE FAILURE

| 1. Does the machine show warning signs before a fault? | Often |
| --- | --- |
| 2. Warning signs observed | Pressure rise; falling permeate flow; rising conductivity; pump noise. |
| 3. How long before failure do warning signs appear? | Several days |
| 4. Earliest indication of a developing fault | Slow rise in membrane differential pressure. |
| 5. Most reliable indication of impending failure | Pressure rise with falling permeate flow. |
| 6. Can an experienced operator detect an upcoming fault through observation? | Sometimes |
| 7. What does the operator normally observe? | Pressure readings, flow readings, conductivity. |

SECTION G: MACHINE SOUND AND NOISE BEHAVIOUR

| 1. Does the machine produce a different sound when developing a fault? | Yes |
| --- | --- |
| 2. Abnormal sound | Whining; humming; rattling |
| 3. Component producing abnormal sound | High-pressure pump |
| 4. Describe the normal machine sound | Steady pump hum. |
| 5. Describe the sound immediately before failure | Rising whine from the pump. |
| 6. Does the abnormal sound increase gradually? | Yes |
| 7. Can an experienced operator identify a fault from sound? | Sometimes |
| 8. Usefulness of automatic sound monitoring | Useful |

SECTION H: VISUAL AND PHYSICAL MACHINE CHANGES

| Observation | Frequency |
| --- | --- |
| Excessive vibration | Rarely |
| Increased temperature | Sometimes |
| Oil leakage | Sometimes |
| Smoke | Never |
| Burning smell | Never |
| Unusual noise | Sometimes |
| Reduced speed | Never |
| Reduced output | Often |
| Increased energy consumption | Often |
| Irregular movement | Never |
| Frequent machine stoppage | Sometimes |

SECTION I: FAULT DETECTION AND DIAGNOSIS

| 1. Fault detection method | Sensors; PLC alarms; operator observation |
| --- | --- |
| 2. Fault cause determination | Sensor readings; operator experience; technician inspection |
| 3. Normal diagnosis time | 1–2 hours |
| 4. Challenges | Lack of historical analysis; hidden membrane condition. |

SECTION J: USE OF SENSORS AND SMART MONITORING

| 1. Does the machine have condition-monitoring sensors? | Yes – pressure, flow and conductivity sensors |
| --- | --- |
| 2. Sensor types | Pressure; flow; conductivity; current |
| 3. Are sensor readings stored for future analysis? | Yes – PLC/HMI records |
| 4. Measurement frequency | Continuously for control variables; event logging |
| 5. Would the company be willing to use sensors for continuous machine-health monitoring? | Yes |

SECTION K: PREDICTIVE MAINTENANCE EXPERT SYSTEM

| 1. Does the company currently use a predictive maintenance system? | No |
| --- | --- |
| 2. Would an intelligent system that predicts possible failure be useful? | Very useful |
| 3. Information the system should monitor | Membrane pressure; permeate flow; conductivity; pump current; fault history. |
| 4. Preferred alert | Dashboard + mobile notification |
| 5. Preferred warning time | Several days |
| 6. Would you trust automated maintenance recommendations? | Only with human confirmation |
| 7. Final maintenance decision should be made by | System recommendation + human approval |

SECTION L: EDGE-BASED MONITORING

| 1. Prefer data processed locally near machine? | Yes |
| --- | --- |
| 2. Advantages | Faster response; continuous monitoring. |
| 3. Internet/network reliability | Reliable |
| 4. Should the system continue when internet is unavailable? | Yes – local edge processing should continue and synchronise data when connectivity returns. |

SECTION M: MAINTENANCE RECORD DATA – SAMPLE ENTRIES

| Date | Parameter / Observation | Fault Suspected | Cause | Maintenance Done | Parts Replaced | Downtime |
| --- | --- | --- | --- | --- | --- | --- |
| 22 / 07 / 2026 | Pressure rising, permeate flow falling | Membrane fouling | Scaling | Membranes cleaned, filters replaced | Cartridge filters | 8 h |
| 10 / 03 / 2026 | Pump seal leaking | Seal wear | Normal ageing | Seal replaced | Pump seal | 3 h |

SECTION N: OVERALL ASSESSMENT

Scale: SA = Strongly Agree; A = Agree; U = Undecided; D = Disagree; SD = Strongly Disagree.

| Statement | Rating |
| --- | --- |
| Machine failures can often be detected before complete breakdown. | SA |
| Machine operating parameters are useful for predicting faults. | SA |
| Machine sound can provide information about machine health. | A |
| Maintenance history is important for predicting future faults. | SA |
| Preventive maintenance reduces unexpected machine breakdown. | SA |
| Continuous machine monitoring would improve maintenance activities. | SA |
| An intelligent predictive maintenance system would reduce machine downtime. | SA |
| Sensor-based monitoring would improve fault detection. | A |
| Automated alerts would help maintenance personnel respond faster. | SA |
| An edge-based system would be useful in an industrial environment. | A |

SECTION O: OPEN-ENDED QUESTIONS

| 1. Most common causes of machine failure | Membrane fouling, pump seal wear, filter clogging, dosing faults. |
| --- | --- |
| 2. Changes observed before serious fault | Pressure rise, permeate flow drop, conductivity rise. |
| 3. Sounds indicating developing fault | Pump whine or hum change. |
| 4. Most useful parameters for predicting failure | Membrane pressure, flow, conductivity. |
| 5. Challenges with current maintenance system | Hidden membrane condition, limited sensors. |
| 6. Desired predictive maintenance system features | Fouling prediction and cleaning alerts. |
| 7. Other information useful for the expert system | Raw-water quality and temperature change membrane life. |